## Appendix B - CI Lighting Tables
|  |  |  | Baseline Lamp or Fixture |  | Proposed Lamp or Fixture |  | 0.001 |  | 336
Retrofit / New Construction | Measure Name | Minimum Lumens | Maximum Lumens | Technology/Baseline Lamp or Fixture Description | Baseline Lamp/Fixture Wattage | Technology/Proposed Lamp or Fixture Description | Proposed Lamp/Fixture Wattage | kW Savings | Incremental Cost | Notes
Retrofit | Omnidirectional Lamps | 120 | 309 | Incandescent | 25 | LED | 4 | 0.021 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 310 | 399 | Incandescent | 25 | LED | 4 | 0.021 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 400 | 749 | Incandescent | 29 | LED | 6.6 | 0.022 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 750 | 899 | Incandescent | 43 | LED | 9.6 | 0.033 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 900 | 1399 | Incandescent | 53 | LED | 13.1 | 0.04 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 1400 | 1999 | Incandescent | 72 | LED | 16 | 0.056 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 2000 | 2999 | Incandescent | 150 | LED | 21.8 | 0.128 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 3000 | 3299 | Incandescent | 200 | LED | 28.9 | 0.171 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 3300 | 3999 | Incandescent | 200 | LED | 28.9 | 0.171 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omnidirectional Lamps | 4000 | 5000 | Incandescent | 300 | LED | 35.7 | 0.264 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 120 | 309 | Incandescent | 25 | LED | 4 | 0.021 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 310 | 399 | Incandescent | 25 | LED | 4 | 0.021 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 400 | 749 | Incandescent | 29 | LED | 6.6 | 0.022 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 750 | 899 | Incandescent | 43 | LED | 9.6 | 0.033 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 900 | 1399 | Incandescent | 53 | LED | 13.1 | 0.04 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 1400 | 1999 | Incandescent | 72 | LED | 16 | 0.056 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 2000 | 2999 | Incandescent | 150 | LED | 21.8 | 0.128 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 3000 | 3299 | Incandescent | 200 | LED | 28.9 | 0.171 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 3300 | 3999 | Incandescent | 200 | LED | 28.9 | 0.171 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
New Construction | Omnidirectional Lamps | 4000 | 5000 | Incandescent | 300 | LED | 35.7 | 0.264 | 1.45 | Omnidirectional Lamps - ENERGY STAR Minimum Luminous Efficacy = 80Lm/W for <90 CRI lamps and 70Lm/W for >=90 CRI lamps
Retrofit | Omni-Directional 3-Way | 1100 | 1999 | Incandescent | 100 | LED | 14.7 | 0.085 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Omni-Directional 3-Way | 2000 | 2700 | Incandescent | 150 | LED | 22.6 | 0.127 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (medium and intermediate bases less than 750 lumens) | 150 | 309 | Incandescent | 25 | LED | 3 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (medium and intermediate bases less than 750 lumens) | 310 | 349 | Incandescent | 25 | LED | 3 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (medium and intermediate bases less than 750 lumens) | 350 | 499 | Incandescent | 40 | LED | 4.7 | 0.035 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (medium and intermediate bases less than 750 lumens) | 500 | 574 | Incandescent | 60 | LED | 5.7 | 0.054 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (medium and intermediate bases less than 750 lumens) | 575 | 649 | Incandescent | 75 | LED | 6.5 | 0.069 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (medium and intermediate bases less than 750 lumens) | 650 | 1000 | Incandescent | 100 | LED | 8.2 | 0.092 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (candelabra bases less than 1050 lumens) | 150 | 309 | Incandescent | 25 | LED | 3.5 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (candelabra bases less than 1050 lumens) | 310 | 349 | Incandescent | 25 | LED | 3.5 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (candelabra bases less than 1050 lumens) | 350 | 499 | Incandescent | 40 | LED | 4.4 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Globe (candelabra bases less than 1050 lumens) | 500 | 574 | Incandescent | 60 | LED | 5.5 | 0.055 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | 160 | 299 | Incandescent | 25 | LED | 2.6 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | 300 | 309 | Incandescent | 40 | LED | 4.3 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | 310 | 499 | Incandescent | 40 | LED | 4.3 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | 500 | 800 | Incandescent | 60 | LED | 5.8 | 0.054 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 120 | 159 | Incandescent | 15 | LED | 1.5 | 0.014 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 160 | 299 | Incandescent | 25 | LED | 2.7 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 300 | 309 | Incandescent | 40 | LED | 4.2 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 310 | 499 | Incandescent | 40 | LED | 4.2 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 500 | 650 | Incandescent | 60 | LED | 5.5 | 0.055 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shape ST) | 250 | 309 | Incandescent | 40 | LED | 6.5 | 0.034 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shape ST) | 310 | 499 | Incandescent | 40 | LED | 6.5 | 0.034 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shape ST) | 500 | 999 | Incandescent | 60 | LED | 8.8 | 0.051 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shape ST) | 1000 | 1500 | Incandescent | 100 | LED | 10 | 0.09 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shape S) | 50 | 75 | Incandescent | 11 | LED | 1 | 0.01 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shape S) | 100 | 120 | Incandescent | 15 | LED | 1.2 | 0.014 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shape S) | 120 | 309 | Incandescent | 25 | LED | 2.25 | 0.023 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Decorative (Shape S) | 310 | 340 | Incandescent | 25 | LED | 2.25 | 0.023 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Omni-Directional 3-Way | 1100 | 1999 | Incandescent | 100 | LED | 14.7 | 0.085 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Omni-Directional 3-Way | 2000 | 2700 | Incandescent | 150 | LED | 22.6 | 0.127 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (medium and intermediate bases less than 750 lumens) | 150 | 309 | Incandescent | 25 | LED | 3 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (medium and intermediate bases less than 750 lumens) | 310 | 349 | Incandescent | 25 | LED | 3 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (medium and intermediate bases less than 750 lumens) | 350 | 499 | Incandescent | 40 | LED | 4.7 | 0.035 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (medium and intermediate bases less than 750 lumens) | 500 | 574 | Incandescent | 60 | LED | 5.7 | 0.054 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (medium and intermediate bases less than 750 lumens) | 575 | 649 | Incandescent | 75 | LED | 6.5 | 0.069 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (medium and intermediate bases less than 750 lumens) | 650 | 1000 | Incandescent | 100 | LED | 8.2 | 0.092 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (candelabra bases less than 1050 lumens) | 150 | 309 | Incandescent | 25 | LED | 3.5 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (candelabra bases less than 1050 lumens) | 310 | 349 | Incandescent | 25 | LED | 3.5 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (candelabra bases less than 1050 lumens) | 350 | 499 | Incandescent | 40 | LED | 4.4 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Globe (candelabra bases less than 1050 lumens) | 500 | 574 | Incandescent | 60 | LED | 5.5 | 0.055 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | 160 | 299 | Incandescent | 25 | LED | 2.6 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | 300 | 309 | Incandescent | 40 | LED | 4.3 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | 310 | 499 | Incandescent | 40 | LED | 4.3 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, medium and intermediate bases less than 750 lumens) | 500 | 800 | Incandescent | 60 | LED | 5.8 | 0.054 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 120 | 159 | Incandescent | 15 | LED | 1.5 | 0.014 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 160 | 299 | Incandescent | 25 | LED | 2.7 | 0.022 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 300 | 309 | Incandescent | 40 | LED | 4.2 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 310 | 499 | Incandescent | 40 | LED | 4.2 | 0.036 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shapes B, BA, C, CA, DC, F, G, T candelabra bases less than 1050 lumens) | 500 | 650 | Incandescent | 60 | LED | 5.5 | 0.055 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shape ST) | 250 | 309 | Incandescent | 40 | LED | 6.5 | 0.034 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shape ST) | 310 | 499 | Incandescent | 40 | LED | 6.5 | 0.034 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shape ST) | 500 | 999 | Incandescent | 60 | LED | 8.8 | 0.051 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shape ST) | 1000 | 1500 | Incandescent | 100 | LED | 10 | 0.09 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shape S) | 50 | 75 | Incandescent | 11 | LED | 1 | 0.01 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shape S) | 100 | 120 | Incandescent | 15 | LED | 1.2 | 0.014 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shape S) | 120 | 309 | Incandescent | 25 | LED | 2.25 | 0.023 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
New Construction | Decorative (Shape S) | 310 | 340 | Incandescent | 25 | LED | 2.25 | 0.023 | 1.66 | Decorative Lamps - ENERGY STAR Minimum Luminous Efficacy = 65Lm/W for all lamps
Retrofit | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 400 | 649 | Incandescent | 50 | LED | 7 | 0.043 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 650 | 899 | Incandescent | 75 | LED | 10.7 | 0.064 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 900 | 1049 | Incandescent | 90 | LED | 13.9 | 0.076 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 1050 | 1199 | Incandescent | 100 | LED | 13.8 | 0.086 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 1200 | 1499 | Incandescent | 120 | LED | 15.9 | 0.104 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 1500 | 1999 | Incandescent | 150 | LED | 18.9 | 0.131 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 2000 | 3299 | Incandescent | 250 | LED | 27.3 | 0.223 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 3300 | 4200 | Incandescent | 250 | LED | 27.3 | 0.223 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR16, R14, R16, etc.) w/ diameter <2.25" (*see exceptions below) | 280 | 309 | Incandescent | 35 | LED | 4.6 | 0.03 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR16, R14, R16, etc.) w/ diameter <2.25" (*see exceptions below) | 310 | 374 | Incandescent | 35 | LED | 4.6 | 0.03 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Reflector lamp types with medium screw bases (PAR16, R14, R16, etc.) w/ diameter <2.25" (*see exceptions below) | 375 | 600 | Incandescent | 50 | LED | 6.4 | 0.044 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *BR30, BR40, or ER40 | 650 | 949 | Incandescent | 65 | LED | 9.3 | 0.056 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *BR30, BR40, or ER41 | 950 | 1099 | Incandescent | 75 | LED | 12.7 | 0.062 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *BR30, BR40, or ER42 | 1100 | 1399 | Incandescent | 85 | LED | 14.4 | 0.071 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *BR30, BR40, or ER43 | 1400 | 1600 | Incandescent | 100 | LED | 16.6 | 0.083 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *BR30, BR40, or ER44 | 1601 | 1800 | Incandescent | 120 | LED | 22.2 | 0.098 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *R20 | 450 | 524 | Incandescent | 40 | LED | 6 | 0.034 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *R21 | 525 | 750 | Incandescent | 45 | LED | 7.1 | 0.038 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *MR16 | 250 | 309 | Incandescent | 20 | LED | 3.8 | 0.016 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *MR17 | 310 | 324 | Incandescent | 20 | LED | 3.8 | 0.016 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *MR18 | 325 | 369 | Incandescent | 25 | LED | 4.8 | 0.02 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | *MR19 | 370 | 400 | Incandescent | 25 | LED | 4.9 | 0.02 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 400 | 649 | Incandescent | 50 | LED | 7 | 0.043 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 650 | 899 | Incandescent | 75 | LED | 10.7 | 0.064 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 900 | 1049 | Incandescent | 90 | LED | 13.9 | 0.076 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 1050 | 1199 | Incandescent | 100 | LED | 13.8 | 0.086 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 1200 | 1499 | Incandescent | 120 | LED | 15.9 | 0.104 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 1500 | 1999 | Incandescent | 150 | LED | 18.9 | 0.131 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 2000 | 3299 | Incandescent | 250 | LED | 27.3 | 0.223 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR20, PAR30(S,L), PAR38, R40, etc.) w/ diameter >2.25" (*see exceptions below) | 3300 | 4200 | Incandescent | 250 | LED | 27.3 | 0.223 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR16, R14, R16, etc.) w/ diameter <2.25" (*see exceptions below) | 280 | 309 | Incandescent | 35 | LED | 4.6 | 0.03 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR16, R14, R16, etc.) w/ diameter <2.25" (*see exceptions below) | 310 | 374 | Incandescent | 35 | LED | 4.6 | 0.03 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | Reflector lamp types with medium screw bases (PAR16, R14, R16, etc.) w/ diameter <2.25" (*see exceptions below) | 375 | 600 | Incandescent | 50 | LED | 6.4 | 0.044 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *BR30, BR40, or ER40 | 650 | 949 | Incandescent | 65 | LED | 9.3 | 0.056 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *BR30, BR40, or ER41 | 950 | 1099 | Incandescent | 75 | LED | 12.7 | 0.062 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *BR30, BR40, or ER42 | 1100 | 1399 | Incandescent | 85 | LED | 14.4 | 0.071 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *BR30, BR40, or ER43 | 1400 | 1600 | Incandescent | 100 | LED | 16.6 | 0.083 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *BR30, BR40, or ER44 | 1601 | 1800 | Incandescent | 120 | LED | 22.2 | 0.098 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *R20 | 450 | 524 | Incandescent | 40 | LED | 6 | 0.034 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *R21 | 525 | 750 | Incandescent | 45 | LED | 7.1 | 0.038 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *MR16 | 250 | 309 | Incandescent | 20 | LED | 3.8 | 0.016 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *MR17 | 310 | 324 | Incandescent | 20 | LED | 3.8 | 0.016 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *MR18 | 325 | 369 | Incandescent | 25 | LED | 4.8 | 0.02 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
New Construction | *MR19 | 370 | 400 | Incandescent | 25 | LED | 4.9 | 0.02 | 1.65 | Directional Lamps - ENERGY STAR Minimum Luminous Efficacy = 70Lm/W for <90 CRI lamps and 61 Lm/W for >=90CRI lamps
Retrofit | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 120 | 309 | Incandescent | 25 | LED | 4 | 0.021 |  | NA
Retrofit | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 310 | 399 | Incandescent | 25 | LED | 4 | 0.021 |  | NA
Retrofit | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 400 | 749 | Incandescent | 29 | LED | 6.6 | 0.022 |  | NA
Retrofit | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 750 | 899 | Incandescent | 43 | LED | 9.6 | 0.033 |  | NA
Retrofit | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 900 | 1399 | Incandescent | 53 | LED | 13.1 | 0.04 |  | NA
Retrofit | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 1400 | 1999 | Incandescent | 72 | LED | 16 | 0.056 |  | NA
New Construction | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 120 | 309 | Incandescent | 25 | LED | 4 | 0.021 |  | NA
New Construction | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 310 | 399 | Incandescent | 25 | LED | 4 | 0.021 |  | NA
New Construction | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 400 | 749 | Incandescent | 29 | LED | 6.6 | 0.022 |  | NA
New Construction | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 750 | 899 | Incandescent | 43 | LED | 9.6 | 0.033 |  | NA
New Construction | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 900 | 1399 | Incandescent | 53 | LED | 13.1 | 0.04 |  | NA
New Construction | Dimmable Twist, Globe, candle, Candelabra Base Lamps, Intermediate Base Lamps | 1400 | 1999 | Incandescent | 72 | LED | 16 | 0.056 |  | NA
Retrofit | LED Downlight Fixtures | NA | NA | Baseline Recessed, Surface, Pendant Downlights | 54.3 | LED Recessed, Surface, Pendant Downlights | 16 | 0.038 | 27 | NA
Retrofit | LED Interior Directional | NA | NA | Baseline Track Lighting | 60.4 | LED Track Lighting | 16 | 0.044 | 59 | NA
Retrofit | LED Interior Directional | NA | NA | Baseline Wall-Wash Fixtures | 17.7 | LED Wall-Wash Fixtures | 16 | 0.002 | 59 | NA
Retrofit | LED Display Case | NA | NA | Baseline Display Case Light Fixture | 36.2/ft | LED Display Case Light Fixture | 4/ft | 0.032/ft | $11/ft | NA
Retrofit | LED Display Case | NA | NA | Baseline Undercabinet Shelf-Mounted Task Light Fixtures | 36.2/ft | LED Undercabinet Shelf-Mounted Task Light Fixtures | 4/ft | 0.032/ft | $11/ft | NA
Retrofit | LED Display Case | NA | NA | Baseline Refrigerated Case Light, Horizontal or Vertical (per foot) | 15.2/ft | LED Refrigerated Case Light, Horizontal or Vertical | 4/ft | 0.011/ft | $11/ft | NA
Retrofit | LED Display Case | NA | NA | Baseline Freezer Case Light, Horizontal or Vertical (per foot) | 18.7/ft | LED Freezer Case Light, Horizontal or Vertical | 4/ft | 0.015/ft | $11/ft | NA
Retrofit | LED Linear Replacement Lamps | 0 | 1200 | F17T8 Standard Lamp - 2 foot | 15 | T8 LED Replacement Lamp (TLED), < 1200 lumens | 13 | 0.002 | 13 | NA
Retrofit | LED Linear Replacement Lamps | 1201 | 2400 | F32T8 Standard Lamp - 4 foot | 28.2 | T8 LED Replacement Lamp (TLED), 1200-2400 lumens | 16 | 0.0122 | 15 | NA
Retrofit | LED Linear Replacement Lamps | 2400 | inf | F32T8/HO Standard Lamp - 4 foot | 41.8 | T8 LED Replacement Lamp (TLED), > 2400 lumens | 16 | 0.0258 | 13 | NA
Retrofit | LED Troffers | 2000 | 3500 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED 2x2 Recessed Light Fixture, 2000-3500 lumens | 16 | 0.041 | 53 | NA
Retrofit | LED Troffers | 3501 | 5000 | 3-Lamp 32w T8 (BF <0.88) | 84.5 | LED 2x2 Recessed Light Fixture, 3501-5000 lumens | 16 | 0.0685 | 69 | NA
Retrofit | LED Troffers | 3000 | 4500 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED 2x4 Recessed Light Fixture, 3000-4500 lumens | 16 | 0.041 | 55 | NA
Retrofit | LED Troffers | 4501 | 6000 | 3-Lamp 32w T8 (BF <0.88) | 84.5 | LED 2x4 Recessed Light Fixture, 4501-6000 lumens | 16 | 0.0685 | 76 | NA
Retrofit | LED Troffers | 6001 | 7500 | 4-Lamp 32w T8 (BF <0.88) | 112.6 | LED 2x4 Recessed Light Fixture, 6001-7500 lumens | 16 | 0.0966 | 104 | NA
Retrofit | LED Troffers | 1500 | 3000 | 1-Lamp 32w T8 (BF<0.91) | 29.1 | LED 1x4 Recessed Light Fixture, 1500-3000 lumens | 16 | 0.0131 | 22 | NA
Retrofit | LED Troffers | 3001 | 4500 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED 1x4 Recessed Light Fixture, 3001-4500 lumens | 16 | 0.041 | 75 | NA
Retrofit | LED Troffers | 4501 | 6000 | 3-Lamp 32w T8 (BF <0.88) | 84.5 | LED 1x4 Recessed Light Fixture, 4501-6000 lumens | 16 | 0.0685 | 83 | NA
Retrofit | LED Linear Ambient Fixtures | 0 | 3000 | 1-Lamp 32w T8 (BF<0.91) | 29.1 | LED Surface & Suspended Linear Fixture, <= 3000 lumens | 16 | 0.0131 | 10 | NA
Retrofit | LED Linear Ambient Fixtures | 3001 | 4500 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED Surface & Suspended Linear Fixture, 3001-4500 lumens | 16 | 0.041 | 52 | NA
Retrofit | LED Linear Ambient Fixtures | 4501 | 6000 | 3-Lamp 32w T8 (BF <0.88) | 84.5 | LED Surface & Suspended Linear Fixture, 4501-6000 lumens | 16 | 0.0685 | 78 | NA
Retrofit | LED Linear Ambient Fixtures | 6001 | 7500 | T5HO 2L-F54T5HO - 4' | 120 | LED Surface & Suspended Linear Fixture, 6001-7500 lumens | 16 | 0.104 | 131 | NA
Retrofit | LED Linear Ambient Fixtures | 7500 | inf | T5HO 3L-F54T5HO - 4' | 180 | LED Surface & Suspended Linear Fixture, > 7500 lumens | 16 | 0.164 | 173 | NA
Retrofit | LED High & Low Bay Fixtures | 0 | 10000 | 3-Lamp T8HO Low-Bay | 157 | LED Low-Bay Fixtures, <= 10,000 lumens | 16 | 0.141 | 42.88 | NA
Retrofit | LED High & Low Bay Fixtures | 10001 | 15000 | 4-Lamp T8HO High-Bay | 196 | LED High-Bay Fixtures, 10,001-15,000 lumens | 16 | 0.18 | 31.94 | NA
Retrofit | LED High & Low Bay Fixtures | 15001 | 20000 | 6-Lamp T8HO High-Bay | 294 | LED High-Bay Fixtures, 15,001-20,000 lumens | 16 | 0.278 | 61.17 | NA
Retrofit | LED High & Low Bay Fixtures | 20001 | 30000 | 8-Lamp T8HO High-Bay | 392 | LED High-Bay Fixtures, 20,001-30,000 lumens | 16 | 0.376 | 51.11 | NA
Retrofit | LED High & Low Bay Fixtures | 30001 | 40000 | 750 Watts Metal Halide | 850 | LED High-Bay Fixtures, 30,001-40,000 lumens | 16 | 0.834 | 113.6 | NA
Retrofit | LED High & Low Bay Fixtures | 40001 | 50000 | 1000 Watts Metal Halide | 1080 | LED High-Bay Fixtures 40,001-50,000 lumens | 16 | 1.064 | 166.55 | NA
Retrofit | LED High & Low Bay Fixtures | 50001 | inf | 1500 Watts Metal Halide | 1610 | LED High-Bay Fixtures >50,000 lumens | 16 | 1.594 | 283.67 | NA
Retrofit | LED Agricultural Interior Fixtures | 0 | 2000 | 1-Lamp 32w T8 (BF <0.91) | 29.1 | LED Ag Interior Fixtures, <= 2,000 lumens | 16 | 0.0131 | 18 | NA
Retrofit | LED Agricultural Interior Fixtures | 2001 | 4000 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED Ag Interior Fixtures, 2,001-4,000 lumens | 16 | 0.041 | 48 | NA
Retrofit | LED Agricultural Interior Fixtures | 4001 | 6000 | 25% 217 Watt EISA Inc, 75% 3L T8 | 121 | LED Ag Interior Fixtures, 4,001-6,000 lumens | 16 | 0.105 | 57 | NA
Retrofit | LED Agricultural Interior Fixtures | 6001 | 8000 | 25% 292 Watt EISA Inc, 75% 4L T8 | 159 | LED Ag Interior Fixtures, 6,001-8,000 lumens | 16 | 0.143 | 88 | NA
Retrofit | LED Agricultural Interior Fixtures | 8001 | 12000 | 200W Pulse Start Metal Halide | 227.3 | LED Ag Interior Fixtures, 8,001-12,000 lumens | 16 | 0.2113 | 168 | NA
Retrofit | LED Agricultural Interior Fixtures | 12001 | 16000 | 320W Pulse Start Metal Halide | 363.6 | LED Ag Interior Fixtures, 12,001-16,000 lumens | 16 | 0.3476 | 151 | NA
Retrofit | LED Agricultural Interior Fixtures | 16001 | 20000 | 350W Pulse Start Metal Halide | 397.7 | LED Ag Interior Fixtures, 16,001-20,000 lumens | 16 | 0.3817 | 205 | NA
Retrofit | LED Agricultural Interior Fixtures | 20000 | inf | (2) 320W Pulse Start Metal Halide | 727.3 | LED Ag Interior Fixtures, > 20,000 lumens | 16 | 0.7113 | 356 | NA
Retrofit | LED Exterior Fixtures | 0 | 5000 | 100W Metal Halide | 113.6 | LED Exterior Fixtures, <= 5,000 lumens | 16 | 0.0976 | 97 | NA
Retrofit | LED Exterior Fixtures | 5001 | 10000 | 175W Pulse Start Metal Halide | 198.9 | LED Exterior Fixtures, 5,001-10,000 lumens | 16 | 0.1829 | 123.81 | NA
Retrofit | LED Exterior Fixtures | 10001 | 15000 | 250W Pulse Start Metal Halide | 284.1 | LED Exterior Fixtures, 10,001-15,000 lumens | 16 | 0.2681 | 134.35 | NA
Retrofit | LED Exterior Fixtures | 15001 | 30000 | 400W Pulse Start Metal Halide | 454.5 | LED Exterior Fixtures, 15,001-30,000 lumens | 16 | 0.4385 | 196.16 | NA
Retrofit | LED Exterior Fixtures | 30001 | 40000 | 750 W Metal Halide | 850 | LED Exterior Fixtures, 30,001-40,000 lumens | 16 | 0.834 | 238.18 | NA
Retrofit | LED Exterior Fixtures | 40001 | 50000 | 1000 W Metal Halide | 1080 | LED Exterior Fixtures, 40,001-50,000 lumens | 16 | 1.064 | 319.31 | NA
Retrofit | LED Exterior Fixtures | 50000 | inf | 1500 W Metal Halide | 1610 | LED Exterior Fixtures, > 50,000 lumens | 16 | 1.594 | 1094.74 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type A | 0 | 5000 | 100W Metal Halide | 100 | LED Mogul Base HID Replacement Lamp, <= 5,000 lumens | 16 | 0.084 | 68 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 0 | 5000 | 100W Metal Halide | 113.6 | LED Mogul Base HID Replacement Lamp, <= 5,000 lumens | 16 | 0.0976 | 68 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type A | 5001 | 10000 | 175W Pulse Start Metal Halide | 175 | LED Mogul Base HID Replacement Lamp, 5,001-10,000 lumens | 16 | 0.159 | 60 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 5001 | 10000 | 175W Pulse Start Metal Halide | 198.9 | LED Mogul Base HID Replacement Lamp, 5,001-10,000 lumens | 16 | 0.1829 | 60 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type A | 10001 | 15000 | 250W Pulse Start Metal Halide | 250 | LED Mogul Base HID Replacement Lamp, 10,001-15,000 lumens | 16 | 0.234 | 129 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 10001 | 15000 | 250W Pulse Start Metal Halide | 284.1 | LED Mogul Base HID Replacement Lamp, 10,001-15,000 lumens | 16 | 0.2681 | 129 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type A | 15001 | 30000 | 400W Pulse Start Metal Halide | 400 | LED Mogul Base HID Replacement Lamp, 15,001-30,000 lumens | 16 | 0.384 | 156 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 15001 | 30000 | 400W Pulse Start Metal Halide | 454.5 | LED Mogul Base HID Replacement Lamp, 15,001-30,000 lumens | 16 | 0.4385 | 156 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type A | 30001 | 40000 | 750 W Metal Halide | 750 | LED Mogul Base HID Replacement Lamp, 30,001-40,000 lumens | 16 | 0.734 | 446 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 30001 | 40000 | 751 W Metal Halide | 850 | LED Mogul Base HID Replacement Lamp, 30,001-40,000 lumens | 16 | 0.834 | 446 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type A | 40000 | inf | 1000 W Metal Halide | 1000 | LED Mogul Base HID Replacement Lamp, > 40,000 lumens | 16 | 0.984 | 629 | NA
Retrofit | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 40000 | inf | 1001 W Metal Halide | 1080 | LED Mogul Base HID Replacement Lamp, > 40,000 lumens | 16 | 1.064 | 629 | NA
New Construction | LED Downlight Fixtures | NA | NA | Baseline Recessed, Surface, Pendant Downlights | 54.3 | LED Recessed, Surface, Pendant Downlights | 16 | 0.0383 | 27 | NA
New Construction | LED Interior Directional | NA | NA | Baseline Track Lighting | 60.4 | LED Track Lighting | 16 | 0.0444 | 59 | NA
New Construction | LED Interior Directional | NA | NA | Baseline Wall-Wash Fixtures | 17.7 | LED Wall-Wash Fixtures | 16 | 0.0017 | 59 | NA
New Construction | LED Display Case | NA | NA | Baseline Display Case Light Fixture | 36.2/ft | LED Display Case Light Fixture | 4/ft | 0.032/ft | $11/ft | NA
New Construction | LED Display Case | NA | NA | Baseline Undercabinet Shelf-Mounted Task Light Fixtures | 36.2/ft | LED Undercabinet Shelf-Mounted Task Light Fixtures | 4/ft | 0.032/ft | $11/ft | NA
New Construction | LED Display Case | NA | NA | Baseline Refrigerated Case Light, Horizontal or Vertical (per foot) | 15.2/ft | LED Refrigerated Case Light, Horizontal or Vertical | 4/ft | 0.011/ft | $11/ft | NA
New Construction | LED Display Case | NA | NA | Baseline Freezer Case Light, Horizontal or Vertical (per foot) | 18.7/ft | LED Freezer Case Light, Horizontal or Vertical | 4/ft | 0.015/ft | $11/ft | NA
New Construction | LED Linear Replacement Lamps | 0 | 1200 | F17T8 Standard Lamp - 2 foot | 15 | T8 LED Replacement Lamp (TLED), < 1200 lumens | 13 | 0.002 | 13 | NA
New Construction | LED Linear Replacement Lamps | 1201 | 2400 | F32T8 Standard Lamp - 4 foot | 28.2 | T8 LED Replacement Lamp (TLED), 1200-2400 lumens | 16 | 0.012 | 15 | NA
New Construction | LED Linear Replacement Lamps | 2400 | inf | F32T8/HO Standard Lamp - 4 foot | 41.8 | T8 LED Replacement Lamp (TLED), > 2400 lumens | 16 | 0.026 | 13 | NA
New Construction | LED Troffers | 2000 | 3500 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED 2x2 Recessed Light Fixture, 2000-3500 lumens | 16 | 0.041 | 53 | NA
New Construction | LED Troffers | 3501 | 5000 | 3-Lamp 32w T8 (BF <0.88) | 84.5 | LED 2x2 Recessed Light Fixture, 3501-5000 lumens | 16 | 0.069 | 69 | NA
New Construction | LED Troffers | 3000 | 4500 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED 2x4 Recessed Light Fixture, 3000-4500 lumens | 16 | 0.041 | 55 | NA
New Construction | LED Troffers | 4501 | 6000 | 3-Lamp 32w T8 (BF <0.88) | 84.5 | LED 2x4 Recessed Light Fixture, 4501-6000 lumens | 16 | 0.069 | 76 | NA
New Construction | LED Troffers | 6001 | 7500 | 4-Lamp 32w T8 (BF <0.88) | 112.6 | LED 2x4 Recessed Light Fixture, 6001-7500 lumens | 16 | 0.097 | 104 | NA
New Construction | LED Troffers | 1500 | 3000 | 1-Lamp 32w T8 (BF<0.91) | 29.1 | LED 1x4 Recessed Light Fixture, 1500-3000 lumens | 16 | 0.013 | 22 | NA
New Construction | LED Troffers | 3001 | 4500 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED 1x4 Recessed Light Fixture, 3001-4500 lumens | 16 | 0.041 | 75 | NA
New Construction | LED Troffers | 4501 | 6000 | 3-Lamp 32w T8 (BF <0.88) | 84.5 | LED 1x4 Recessed Light Fixture, 4501-6000 lumens | 16 | 0.069 | 83 | NA
New Construction | LED Linear Ambient Fixtures | 0 | 3000 | 1-Lamp 32w T8 (BF<0.91) | 29.1 | LED Surface & Suspended Linear Fixture, <= 3000 lumens | 16 | 0.013 | 10 | NA
New Construction | LED Linear Ambient Fixtures | 3001 | 4500 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED Surface & Suspended Linear Fixture, 3001-4500 lumens | 16 | 0.041 | 52 | NA
New Construction | LED Linear Ambient Fixtures | 4501 | 6000 | 3-Lamp 32w T8 (BF <0.88) | 84.5 | LED Surface & Suspended Linear Fixture, 4501-6000 lumens | 16 | 0.069 | 78 | NA
New Construction | LED Linear Ambient Fixtures | 6001 | 7500 | T5HO 2L-F54T5HO - 4' | 120 | LED Surface & Suspended Linear Fixture, 6001-7500 lumens | 16 | 0.104 | 131 | NA
New Construction | LED Linear Ambient Fixtures | 7500 | inf | T5HO 3L-F54T5HO - 4' | 180 | LED Surface & Suspended Linear Fixture, > 7500 lumens | 16 | 0.164 | 173 | NA
New Construction | LED High & Low Bay Fixtures | 0 | 10000 | 3-Lamp T8HO Low-Bay | 157 | LED Low-Bay Fixtures, <= 10,000 lumens | 16 | 0.141 | 42.88 | NA
New Construction | LED High & Low Bay Fixtures | 10001 | 15000 | 4-Lamp T8HO High-Bay | 196 | LED High-Bay Fixtures, 10,001-15,000 lumens | 16 | 0.18 | 31.94 | NA
New Construction | LED High & Low Bay Fixtures | 15001 | 20000 | 6-Lamp T8HO High-Bay | 294 | LED High-Bay Fixtures, 15,001-20,000 lumens | 16 | 0.278 | 61.17 | NA
New Construction | LED High & Low Bay Fixtures | 20001 | 30000 | 8-Lamp T8HO High-Bay | 392 | LED High-Bay Fixtures, 20,001-30,000 lumens | 16 | 0.376 | 51.11 | NA
New Construction | LED High & Low Bay Fixtures | 30001 | 40000 | 750 Watts Metal Halide | 850 | LED High-Bay Fixtures, 30,001-40,000 lumens | 16 | 0.834 | 113.6 | NA
New Construction | LED High & Low Bay Fixtures | 40001 | 50000 | 1000 Watts Metal Halide | 1080 | LED High-Bay Fixtures 40,001-50,000 lumens | 16 | 1.064 | 166.55 | NA
New Construction | LED High & Low Bay Fixtures | 50001 | inf | 1500 Watts Metal Halide | 1610 | LED High-Bay Fixtures >50,000 lumens | 16 | 1.594 | 283.67 | NA
New Construction | LED Agricultural Interior Fixtures | 0 | 2000 | 1-Lamp 32w T8 (BF <0.91) | 29.1 | LED Ag Interior Fixtures, <= 2,000 lumens | 16 | 0.013 | 18 | NA
New Construction | LED Agricultural Interior Fixtures | 2001 | 4000 | 2-Lamp 32w T8 (BF <0.89) | 57 | LED Ag Interior Fixtures, 2,001-4,000 lumens | 16 | 0.041 | 48 | NA
New Construction | LED Agricultural Interior Fixtures | 4001 | 6000 | 25% 217 Watt EISA Inc, 75% 3L T8 | 121 | LED Ag Interior Fixtures, 4,001-6,000 lumens | 16 | 0.105 | 57 | NA
New Construction | LED Agricultural Interior Fixtures | 6001 | 8000 | 25% 292 Watt EISA Inc, 75% 4L T8 | 159 | LED Ag Interior Fixtures, 6,001-8,000 lumens | 16 | 0.143 | 88 | NA
New Construction | LED Agricultural Interior Fixtures | 8001 | 12000 | 200W Pulse Start Metal Halide | 227.3 | LED Ag Interior Fixtures, 8,001-12,000 lumens | 16 | 0.211 | 168 | NA
New Construction | LED Agricultural Interior Fixtures | 12001 | 16000 | 320W Pulse Start Metal Halide | 363.6 | LED Ag Interior Fixtures, 12,001-16,000 lumens | 16 | 0.348 | 151 | NA
New Construction | LED Agricultural Interior Fixtures | 16001 | 20000 | 350W Pulse Start Metal Halide | 397.7 | LED Ag Interior Fixtures, 16,001-20,000 lumens | 16 | 0.382 | 205 | NA
New Construction | LED Agricultural Interior Fixtures | 20000 | inf | (2) 320W Pulse Start Metal Halide | 727.3 | LED Ag Interior Fixtures, > 20,000 lumens | 16 | 0.711 | 356 | NA
New Construction | LED Exterior Fixtures | 0 | 5000 | 100W Metal Halide | 113.6 | LED Exterior Fixtures, <= 5,000 lumens | 16 | 0.098 | 97 | NA
New Construction | LED Exterior Fixtures | 5001 | 10000 | 175W Pulse Start Metal Halide | 198.9 | LED Exterior Fixtures, 5,001-10,000 lumens | 16 | 0.183 | 123.81 | NA
New Construction | LED Exterior Fixtures | 10001 | 15000 | 250W Pulse Start Metal Halide | 284.1 | LED Exterior Fixtures, 10,001-15,000 lumens | 16 | 0.268 | 134.35 | NA
New Construction | LED Exterior Fixtures | 15001 | 30000 | 400W Pulse Start Metal Halide | 454.5 | LED Exterior Fixtures, 15,001-30,000 lumens | 16 | 0.439 | 196.16 | NA
New Construction | LED Exterior Fixtures | 30001 | 40000 | 750 W Metal Halide | 850 | LED Exterior Fixtures, 30,001-40,000 lumens | 16 | 0.834 | 238.18 | NA
New Construction | LED Exterior Fixtures | 40001 | 50000 | 1000 W Metal Halide | 1080 | LED Exterior Fixtures, 40,001-50,000 lumens | 16 | 1.064 | 319.31 | NA
New Construction | LED Exterior Fixtures | 50000 | inf | 1500 W Metal Halide | 1610 | LED Exterior Fixtures, > 50,000 lumens | 16 | 1.594 | 1094.74 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type A | 0 | 5000 | 100W Metal Halide | 100 | LED Mogul Base HID Replacement Lamp, <= 5,000 lumens | 16 | 0.084 | 68 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 0 | 5000 | 100W Metal Halide | 113.6 | LED Mogul Base HID Replacement Lamp, <= 5,000 lumens | 16 | 0.098 | 68 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type A | 5001 | 10000 | 175W Pulse Start Metal Halide | 175 | LED Mogul Base HID Replacement Lamp, 5,001-10,000 lumens | 16 | 0.159 | 60 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 5001 | 10000 | 175W Pulse Start Metal Halide | 198.9 | LED Mogul Base HID Replacement Lamp, 5,001-10,000 lumens | 16 | 0.183 | 60 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type A | 10001 | 15000 | 250W Pulse Start Metal Halide | 250 | LED Mogul Base HID Replacement Lamp, 10,001-15,000 lumens | 16 | 0.234 | 129 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 10001 | 15000 | 250W Pulse Start Metal Halide | 284.1 | LED Mogul Base HID Replacement Lamp, 10,001-15,000 lumens | 16 | 0.268 | 129 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type A | 15001 | 30000 | 400W Pulse Start Metal Halide | 400 | LED Mogul Base HID Replacement Lamp, 15,001-30,000 lumens | 16 | 0.384 | 156 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 15001 | 30000 | 400W Pulse Start Metal Halide | 454.5 | LED Mogul Base HID Replacement Lamp, 15,001-30,000 lumens | 16 | 0.439 | 156 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type A | 30001 | 40000 | 750 W Metal Halide | 750 | LED Mogul Base HID Replacement Lamp, 30,001-40,000 lumens | 16 | 0.734 | 446 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 30001 | 40000 | 751 W Metal Halide | 850 | LED Mogul Base HID Replacement Lamp, 30,001-40,000 lumens | 16 | 0.834 | 446 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type A | 40000 | inf | 1000 W Metal Halide | 1000 | LED Mogul Base HID Replacement Lamp, > 40,000 lumens | 16 | 0.984 | 629 | NA
New Construction | LED Mogul Base HID Replacement Lamps Type B (if unknown, assume Type B) | 40000 | inf | 1001 W Metal Halide | 1080 | LED Mogul Base HID Replacement Lamp, > 40,000 lumens | 16 | 1.064 | 629 | NA
Retrofit | 4-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | 200 Watt Pulse Start Metal-Halide | 232 | 4-Lamp HPT8 w/ High-BF Ballast High-Bay | 147.2 | 0.085 | 200 | NA
Retrofit | 4-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | 250 Watt Metal Halide | 295 | 4-Lamp HPT8 w/ High-BF Ballast High-Bay | 147.2 | 0.148 | 200 | NA
Retrofit | 6-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | 320 Watt Pulse Start Metal-Halide | 348.8 | 6-Lamp HPT8 w/ High-BF Ballast High-Bay | 220.8 | 0.128 | 225 | NA
Retrofit | 6-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | 400 Watt Pulse Start Metal Halide | 455 | 6-Lamp HPT8 w/ High-BF Ballast High-Bay | 220.8 | 0.234 | 225 | NA
Retrofit | 8-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 320 PSMH | 476 | 8-Lamp HPT8 w/ High-BF Ballast High-Bay | 294.4 | 0.182 | 250 | NA
Retrofit | 8-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 400 W Metal Halide | 618 | 8-Lamp HPT8 w/ High-BF Ballast High-Bay | 292.4 | 0.326 | 250 | NA
Retrofit | 1-Lamp HPT8-high performance 32 w lamp | NA | NA | 1-Lamp Standard F32T8 w/ Elec. Ballast | 28.16 | 1-Lamp HPT8-high performance 32 w lamp | 24.64 | 0.004 | 50 | NA
Retrofit | 1-Lamp HPT8-high performance 28 w lamp | NA | NA | 1-Lamp Standard F32T8 w/ Elec. Ballast | 28.16 | 1-Lamp HPT8-high performance 28 w lamp | 21.56 | 0.007 | 55 | NA
Retrofit | 1-Lamp HPT8-high performance 25 w lamp | NA | NA | 1-Lamp Standard F32T8 w/ Elec. Ballast | 28.16 | 1-Lamp HPT8-high performance 25 w lamp | 19.25 | 0.009 | 60 | NA
Retrofit | 2-Lamp HPT8 -high performance 32 w lamp | NA | NA | 2-Lamp Standard F32T8 w/ Elec. Ballast | 56.32 | 2-Lamp HPT8 -high performance 32 w lamp | 49.28 | 0.007 | 65 | NA
Retrofit | 2-Lamp HPT8-high performance 28 w lamp | NA | NA | 2-Lamp Standard F32T8 w/ Elec. Ballast | 56.32 | 2-Lamp HPT8-high performance 28 w lamp | 43.12 | 0.013 | 50 | NA
Retrofit | 2-Lamp HPT8-high performance 25 w lamp | NA | NA | 2-Lamp Standard F32T8 w/ Elec. Ballast | 56.32 | 2-Lamp HPT8-high performance 25 w lamp | 38.5 | 0.018 | 55 | NA
Retrofit | 3-Lamp HPT8-high performance 32 w lamp | NA | NA | 3-Lamp Standard F32T8 w/ Elec. Ballast | 84.48 | 3-Lamp HPT8-high performance 32 w lamp | 73.92 | 0.011 | 60 | NA
Retrofit | 3-Lamp HPT8-high performance 28 w lamp | NA | NA | 3-Lamp Standard F32T8 w/ Elec. Ballast | 84.48 | 3-Lamp HPT8-high performance 28 w lamp | 64.68 | 0.02 | 65 | NA
Retrofit | 3-Lamp HPT8-high performance 25 w lamp | NA | NA | 3-Lamp Standard F32T8 w/ Elec. Ballast | 84.48 | 3-Lamp HPT8-high performance 25 w lamp | 57.75 | 0.027 | 50 | NA
Retrofit | 4-Lamp HPT8 -high performance 32 w lamp | NA | NA | 4-Lamp Standard F32T8 w/ Elec. Ballast | 112.64 | 4-Lamp HPT8 -high performance 32 w lamp | 98.56 | 0.014 | 55 | NA
Retrofit | 4-Lamp HPT8-high performance 28 w lamp | NA | NA | 4-Lamp Standard F32T8 w/ Elec. Ballast | 112.64 | 4-Lamp HPT8-high performance 28 w lamp | 86.24 | 0.026 | 60 | NA
Retrofit | 4-Lamp HPT8-high performance 25 w lamp | NA | NA | 4-Lamp Standard F32T8 w/ Elec. Ballast | 112.64 | 4-Lamp HPT8-high performance 25 w lamp | 77 | 0.036 | 65 | NA
Retrofit | 2-lamp High-Performance HPT8 Troffer | NA | NA | 3-Lamp F32T8 w/ Elec. Ballast | 84.48 | 2-lamp High-Performance HPT8 Troffer | 49.28 | 0.035 | 50 | NA
New Construction | 4-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | 200 Watt Pulse Start Metal-Halide | 232 | 4-Lamp HPT8 w/ High-BF Ballast High-Bay | 147.2 | 0.085 | 55 | NA
New Construction | 4-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | 250 Watt Metal Halide | 295 | 4-Lamp HPT8 w/ High-BF Ballast High-Bay | 147.2 | 0.148 | 60 | NA
New Construction | 6-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | 320 Watt Pulse Start Metal-Halide | 348.8 | 6-Lamp HPT8 w/ High-BF Ballast High-Bay | 220.8 | 0.128 | 65 | NA
New Construction | 6-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | 400 Watt Pulse Start Metal Halide | 455 | 6-Lamp HPT8 w/ High-BF Ballast High-Bay | 220.8 | 0.234 | 100 | NA
New Construction | 8-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 320 PSMH | 476 | 8-Lamp HPT8 w/ High-BF Ballast High-Bay | 294.4 | 0.182 | 75 | NA
New Construction | 8-Lamp HPT8 w/ High-BF Ballast High-Bay | NA | NA | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 400 W Metal Halide | 618 | 8-Lamp HPT8 w/ High-BF Ballast High-Bay | 292.4 | 0.326 | 75 | NA
New Construction | 1-Lamp HPT8-high performance 32 w lamp | NA | NA | 1-Lamp Standard F32T8 w/ Elec. Ballast | 28.16 | 1-Lamp HPT8-high performance 32 w lamp | 24.64 | 0.004 | 15 | NA
New Construction | 1-Lamp HPT8-high performance 28 w lamp | NA | NA | 1-Lamp Standard F32T8 w/ Elec. Ballast | 28.16 | 1-Lamp HPT8-high performance 28 w lamp | 21.56 | 0.007 | 15 | NA
New Construction | 1-Lamp HPT8-high performance 25 w lamp | NA | NA | 1-Lamp Standard F32T8 w/ Elec. Ballast | 28.16 | 1-Lamp HPT8-high performance 25 w lamp | 19.25 | 0.009 | 15 | NA
New Construction | 2-Lamp HPT8 -high performance 32 w lamp | NA | NA | 2-Lamp Standard F32T8 w/ Elec. Ballast | 56.32 | 2-Lamp HPT8 -high performance 32 w lamp | 49.28 | 0.007 | 18 | NA
New Construction | 2-Lamp HPT8-high performance 28 w lamp | NA | NA | 2-Lamp Standard F32T8 w/ Elec. Ballast | 56.32 | 2-Lamp HPT8-high performance 28 w lamp | 43.12 | 0.013 | 18 | NA
New Construction | 2-Lamp HPT8-high performance 25 w lamp | NA | NA | 2-Lamp Standard F32T8 w/ Elec. Ballast | 56.32 | 2-Lamp HPT8-high performance 25 w lamp | 38.5 | 0.018 | 18 | NA
New Construction | 3-Lamp HPT8-high performance 32 w lamp | NA | NA | 3-Lamp Standard F32T8 w/ Elec. Ballast | 84.48 | 3-Lamp HPT8-high performance 32 w lamp | 73.92 | 0.011 | 20 | NA
New Construction | 3-Lamp HPT8-high performance 28 w lamp | NA | NA | 3-Lamp Standard F32T8 w/ Elec. Ballast | 84.48 | 3-Lamp HPT8-high performance 28 w lamp | 64.68 | 0.02 | 20 | NA
New Construction | 3-Lamp HPT8-high performance 25 w lamp | NA | NA | 3-Lamp Standard F32T8 w/ Elec. Ballast | 84.48 | 3-Lamp HPT8-high performance 25 w lamp | 57.75 | 0.027 | 20 | NA
New Construction | 4-Lamp HPT8 -high performance 32 w lamp | NA | NA | 4-Lamp Standard F32T8 w/ Elec. Ballast | 112.64 | 4-Lamp HPT8 -high performance 32 w lamp | 98.56 | 0.014 | 23 | NA
New Construction | 4-Lamp HPT8-high performance 28 w lamp | NA | NA | 4-Lamp Standard F32T8 w/ Elec. Ballast | 112.64 | 4-Lamp HPT8-high performance 28 w lamp | 86.24 | 0.026 | 23 | NA
New Construction | 4-Lamp HPT8-high performance 25 w lamp | NA | NA | 4-Lamp Standard F32T8 w/ Elec. Ballast | 112.64 | 4-Lamp HPT8-high performance 25 w lamp | 77 | 0.036 | 23 | NA
New Construction | 2-lamp High-Performance HPT8 Troffer | NA | NA | 3-Lamp F32T8 w/ Elec. Ballast | 84.48 | 2-lamp High-Performance HPT8 Troffer | 49.28 | 0.035 | 100 | NA
Retrofit | RW T8 - F28T8 Lamp | NA | NA | F32 T8 Standard Lamp | 28.16 | RW T8 - F28T8 Lamp | 24.64 | 0.004 | 2 | NA
Retrofit | RWT8 F2T8 Extra Life Lamp | NA | NA | F32 T8 Standard Lamp | 28.16 | RWT8 F2T8 Extra Life Lamp | 24.64 | 0.004 | 2 | NA
Retrofit | RWT8 - F32/25W T8 Lamp | NA | NA | F32 T8 Standard Lamp | 28.16 | RWT8 - F32/25W T8 Lamp | 22 | 0.006 | 2 | NA
Retrofit | RWT8 - F32/25W T8 Lamp Extra Life | NA | NA | F32 T8 Standard Lamp | 28.16 | RWT8 - F32/25W T8 Lamp Extra Life | 22 | 0.006 | 2 | NA
Retrofit | RWT8 F17T8 Lamp - 2 ft | NA | NA | F17 T8 Standard Lamp - 2ft | 14.96 | RWT8 F17T8 Lamp - 2 ft | 14.08 | 0.001 | 2 | NA
Retrofit | RWT8 F25T8 Lamp - 3 ft | NA | NA | F25 T8 Standard Lamp - 3ft | 22 | RWT8 F25T8 Lamp - 3 ft | 20.24 | 0.002 | 2 | NA
Retrofit | RWT8 F30T8 Lamp - 6' Utube | NA | NA | F32 T8 Standard Utube | 28.16 | RWT8 F30T8 Lamp - 6' Utube | 26.4 | 0.002 | 2 | NA
Retrofit | RWT8 F29T8 Lamp - Utube | NA | NA | F32 T8 Standard Utube | 28.16 | RWT8 F29T8 Lamp - Utube | 25.52 | 0.003 | 2 | NA
Retrofit | RWT8 F96T8 Lamp - 8 ft | NA | NA | F96 T8 Standard Lamp - 8 ft | 61.6 | RWT8 F96T8 Lamp - 8 ft | 57.2 | 0.004 | 2 | NA
New Construction | RW T8 - F28T8 Lamp | NA | NA | F32 T8 Standard Lamp | 28.16 | RW T8 - F28T8 Lamp | 24.64 | 0.004 | 2 | NA
New Construction | RWT8 F2T8 Extra Life Lamp | NA | NA | F32 T8 Standard Lamp | 28.16 | RWT8 F2T8 Extra Life Lamp | 24.64 | 0.004 | 2 | NA
New Construction | RWT8 - F32/25W T8 Lamp | NA | NA | F32 T8 Standard Lamp | 28.16 | RWT8 - F32/25W T8 Lamp | 22 | 0.006 | 2 | NA
New Construction | RWT8 - F32/25W T8 Lamp Extra Life | NA | NA | F32 T8 Standard Lamp | 28.16 | RWT8 - F32/25W T8 Lamp Extra Life | 22 | 0.006 | 2 | NA
New Construction | RWT8 F17T8 Lamp - 2 ft | NA | NA | F17 T8 Standard Lamp - 2ft | 14.96 | RWT8 F17T8 Lamp - 2 ft | 14.08 | 0.001 | 2 | NA
New Construction | RWT8 F25T8 Lamp - 3 ft | NA | NA | F25 T8 Standard Lamp - 3ft | 22 | RWT8 F25T8 Lamp - 3 ft | 20.24 | 0.002 | 2 | NA
New Construction | RWT8 F30T8 Lamp - 6' Utube | NA | NA | F32 T8 Standard Utube | 28.16 | RWT8 F30T8 Lamp - 6' Utube | 26.4 | 0.002 | 2 | NA
New Construction | RWT8 F29T8 Lamp - Utube | NA | NA | F32 T8 Standard Utube | 28.16 | RWT8 F29T8 Lamp - Utube | 25.52 | 0.003 | 2 | NA
New Construction | RWT8 F96T8 Lamp - 8 ft | NA | NA | F96 T8 Standard Lamp - 8 ft | 61.6 | RWT8 F96T8 Lamp - 8 ft | 57.2 | 0.004 | 2 | NA
Retrofit | 2-Lamp T5 High-Bay | NA | NA | 200 Watt Pulse Start Metal-Halide | 232 | 2-Lamp T5 High-Bay | 180 | 0.052 | 100 | NA
Retrofit | 3-Lamp T5 High-Bay | NA | NA | 200 Watt Pulse Start Metal-Halide | 232 | 3-Lamp T5 High-Bay | 180 | 0.052 | 100 | NA
Retrofit | 4-Lamp T5 High-Bay | NA | NA | 320 Watt Pulse Start Metal-Halide | 350 | 4-Lamp T5 High-Bay | 240 | 0.11 | 100 | NA
Retrofit | 6-Lamp T5 High-Bay | NA | NA | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 320 PSMH | 476 | 6-Lamp T5 High-Bay | 360 | 0.116 | 100 | NA
Retrofit | 1-Lamp T5 Troffer/Wrap | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 44 | 1-Lamp T5 Troffer/Wrap | 32 | 0.012 | 40 | NA
Retrofit | 2-Lamp T5 Troffer/Wrap | NA | NA | 3-Lamp F32T8 Equivalent w/ Elec. Ballast | 88 | 2-Lamp T5 Troffer/Wrap | 64 | 0.024 | 40 | NA
Retrofit | 1-Lamp T5 Industrial/Strip | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 44 | 1-Lamp T5 Industrial/Strip | 32 | 0.012 | 30 | NA
Retrofit | 2-Lamp T5 Industrial/Strip | NA | NA | 3-Lamp F32T8 Equivalent w/ Elec. Ballast | 88 | 2-Lamp T5 Industrial/Strip | 64 | 0.024 | 30 | NA
Retrofit | 3-Lamp T5 Industrial/Strip | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 132 | 3-Lamp T5 Industrial/Strip | 96 | 0.036 | 30 | NA
Retrofit | 4-Lamp T5 Industrial/Strip | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 178 | 4-Lamp T5 Industrial/Strip | 128 | 0.05 | 30 | NA
Retrofit | 1-Lamp T5 Indirect | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 44 | 1-Lamp T5 Indirect | 32 | 0.012 | 30 | NA
Retrofit | 2-Lamp T5 Indirect | NA | NA | 3-Lamp F32T8 Equivalent w/ Elec. Ballast | 88 | 2-Lamp T5 Indirect | 64 | 0.024 | 30 | NA
New Construction | 2-Lamp T5 High-Bay | NA | NA | 200 Watt Pulse Start Metal-Halide | 232 | 2-Lamp T5 High-Bay | 180 | 0.052 | 100 | NA
New Construction | 3-Lamp T5 High-Bay | NA | NA | 200 Watt Pulse Start Metal-Halide | 232 | 3-Lamp T5 High-Bay | 180 | 0.052 | 100 | NA
New Construction | 4-Lamp T5 High-Bay | NA | NA | 320 Watt Pulse Start Metal-Halide | 350 | 4-Lamp T5 High-Bay | 240 | 0.11 | 100 | NA
New Construction | 6-Lamp T5 High-Bay | NA | NA | Proportionally Adjusted according to 6-Lamp HPT8 Equivalent to 320 PSMH | 476 | 6-Lamp T5 High-Bay | 360 | 0.116 | 100 | NA
New Construction | 1-Lamp T5 Troffer/Wrap | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 44 | 1-Lamp T5 Troffer/Wrap | 32 | 0.012 | 40 | NA
New Construction | 2-Lamp T5 Troffer/Wrap | NA | NA | 3-Lamp F32T8 Equivalent w/ Elec. Ballast | 88 | 2-Lamp T5 Troffer/Wrap | 64 | 0.024 | 40 | NA
New Construction | 1-Lamp T5 Industrial/Strip | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 44 | 1-Lamp T5 Industrial/Strip | 32 | 0.012 | 30 | NA
New Construction | 2-Lamp T5 Industrial/Strip | NA | NA | 3-Lamp F32T8 Equivalent w/ Elec. Ballast | 88 | 2-Lamp T5 Industrial/Strip | 64 | 0.024 | 30 | NA
New Construction | 3-Lamp T5 Industrial/Strip | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 132 | 3-Lamp T5 Industrial/Strip | 96 | 0.036 | 30 | NA
New Construction | 4-Lamp T5 Industrial/Strip | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 178 | 4-Lamp T5 Industrial/Strip | 128 | 0.05 | 30 | NA
New Construction | 1-Lamp T5 Indirect | NA | NA | Proportionally adjusted according to 2-Lamp T5 Equivalent to 3-Lamp T8 | 44 | 1-Lamp T5 Indirect | 32 | 0.012 | 30 | NA
New Construction | 2-Lamp T5 Indirect | NA | NA | 3-Lamp F32T8 Equivalent w/ Elec. Ballast | 88 | 2-Lamp T5 Indirect | 64 | 0.024 | 30 | NA
Retrofit | LED Exit Sign | NA | NA | INX | 35 | LED | 2 | 0.033 | 32.5 | NA
Retrofit | LED Exit Sign | NA | NA | CFL | 7 | LED | 2 | 0.005 | 32.5 | NA
Retrofit | LED Exit Sign | NA | NA | CFL | 7 | LED | 4 | 0.003 | 32.5 | NA
Retrofit | LED Exit Sign | NA | NA | Unk | 7 | LED | 2 | 0.005 | 32.5 | NA
New Construction | LED Exit Sign | NA | NA | INX | 35 | LED | 2 | 0.033 | 32.5 | NA
New Construction | LED Exit Sign | NA | NA | CFL | 7 | LED | 2 | 0.005 | 32.5 | NA
New Construction | LED Exit Sign | NA | NA | CFL | 7 | LED | 4 | 0.003 | 32.5 | NA
New Construction | LED Exit Sign | NA | NA | Unk | 7 | LED | 2 | 0.005 | 32.5 | NA